Design  and Cost Analysis of an autonomous brackish water reverse osmosis (BWRO) desalination plant powered by photovoltaic cells and battery bank:

Case study in Nicosia, Cyprus

Essam Sh. Mohamed, Dimitri Manolakos, Spyros Kyritsis, Peter Soldatos*

Agricultural University of Athens

Faculty of Natural Resources & Agricultural Engineering

*Agribusiness Management Laboratory

Dept of Agricultural Economics & Rural Development

75 Iera Odos, Street, GR 11855 Athens, Greece

email  esamsh@aua.gr

International Conference on Desalination Costing, Hawaii Grand Hotel, Limassol, Cyprus,

6–7 Dec. 2004

Introduction

In Cyprus, water is becoming one of the most important resources and a prerequisite for development. The exploitation of the water resources has been impressive when compared to other countries of the same size and level of development.

Unfortunately, in spite of the persistent effort that has been put, the quantities of water available for domestic and irrigation purposes are inadequate, because of the reduction in both rainfall and flow of water into the dams,. As a result, in the past few years water-rationing measures were introduced with adverse effects on all fields of activitiy.

In August 2003 the ADIRA project (Autonomous Desalination System concepts for sea water and brackish water in rural areas with renewable energies – Potential, Technologies, Field Experience, Socio-technical and Socio-economic impacts) was initiated with main goal to help to overcome the fresh water shortage problems in MENA (Middle East and North Africa) countries including Cyprus.

The project has three main goals:

- To install Autonomous Desalination Systems (ADS) in Cyprus, Egypt, Morocco, Jordan and Turkey.

- To prepare Master Plans for ADS installations in these countries.

- To develop Decision Support Tools for future investors, installers and operators of ADS.

The economics and the original design of the Cyprus desalination unit as well as the associated Photovoltaic system is presented here. The ADS unit will supply fresh water as a portion of the total water needs of a Sporting Centre in Nicosia. The feed water is brackish (2500 ppm) taken from a borehole. This desalination unit is designed to deliver an average of 50 m3/day throughout the year.

System description

Energy production and storage subsystem

The PV array consists of PV modules with total peak power of 10 kW; the energy produced by PV array is transferred through the DC/DC charge controller (200 A current capacity) to a battery bank of 1900 Ah-48 V capable of storing enough energy for one summer day of the system operation, the stored energy is then transferred to the feed and the high pressure pumps through a DC/AC inverter of 9 kW to provide the starting and operating current of the two induction motors.

The Reverse Osmosis (RO) subsystem

The RO subsystem consists of the feed pump that pumps brackish water from the intake well to the pre-treatment system and then to the high pressure pump. The size of the feed pump assembly depends on the depth of the intake well, the distance between the well and the RO system plus the input pressure to the high pressure pump, the flow rate required and the several head losses in the pipes. A typical centrifugal pump of 5 m3/hr was used in this design. A positive displacement or multistage centrifugal high pressure pump (4.5 kW) is used to pump the feed water through the RO membrane. The reverse osmosis membranes will have at least 42% recovery ratio and fresh water flow rate of 2.1 m3/hr. The fresh water is post treated after the RO system and then stored in a water tank. The brine disposal is performed through a discharge well, see Fig.1.

Design summary:

PV array Peak power of PV array 10 kW PV area required 350 m2 Current capacity of the charge controller 200 A Battery bank Capacity 1900 Ah Battery voltage 48 V Inverter power 10 kW BWRO system Total number of membranes 8 Number of pressure vessels 2 Number of membranes in pressure vessel 4 Permeate flow 2.1 m3/h Recovery Permeate quality <500 ppm Installed power 5.5 kW

The autonomous brackish water desalination unit layout

The ADIRA project is co-funded by the European Commission within the Euro-Mediterranean Regional Programme for Local Water Management, Contract

No: ME8/AIDCO/2001/0515/59610.

Financial calculation of cost and evaluation of investment